## IMONI-0047_TTiMBLE26000K004_24_
IMONI ASSEMBLY TEST REPORT
Report No: | iMoni-SRMS-0544
Assembly Sr. No. | TTiMGPH26000K194
DateTime: | 2026-09-09 11:40
TestLevel: | iMoni Assembly
DeviceIP: | 192.168.0.126 | CPU Sr. No. | Base PCB Sr. No. | Camera Sr. No. | PSU Sr. No.
TotalTests: | 16 | 376 | 133 | 138 | LB/D/26/1542
Sr. No. | TestName | Status | Total Checks | Reason | Remarks
1 | Visual Test | PASSED |  | Visual inspection passed successfully
2 | Burn-In Test | PASSED |  | Burn-In test passed successfully
3 | Fan Test | PASSED | 9
4 | Limit Switch Test | PASSED | 3
5 | Fire Alarm Test | PASSED | 3
6 | Water Leakage Test | PASSED | 3
7 | EM Lock through Keypad | PASSED | 3
8 | EM Lock through eMS | PASSED | 3
9 | Water Logging Test | PASSED | 3
10 | Humidity Test | PASSED | 1
11 | Inside Temperature Test | PASSED | 1
12 | Outside Temperature Test | PASSED | 1
13 | Non - Critical Load Test | PASSED | 3
14 | Camera Test | PASSED | 1
15 | Fan-Fail Test Test | PASSED | 2
16 | HUPS | PASSED | 1
OPERATOR: |  |  | APPROVED BY: